## 温升2 实际需要的点位
Beginning time: 09:53 Ending time: 17:31 |  |  | Test duration:7h38min |  | Final | Rise | Limit
Test date: 2025-03-11 |  |  | Temperature record |  | unit:℃ | K | K
Tr2. | 1200A |  | Ambient-avg
Test-point | Test position | phase | Tester No.&TC Time
1 | Incoming terminal of supply | L1 | 1 | 107 |  |  | 70
2 |  | L2 | 1 | 108 |  |  | 70
3 |  | L3 | 1 | 110 |  |  | 70
4 | Support of incoming busbar | L1 | 1 | 105 |  |  | 90
5 |  | L2 | 1 | 109 |  |  | 90
6 |  | L3 | 1 | 104 |  |  | 90
7 | Bolted joint between incoming busbar and ACB incoming busbar | L1 | 1 | 101 |  |  | 90
8 |  | L2 | 1 | 102 |  |  | 90
9 |  | L3 | 1 | 103 |  |  | 90
10 | Support of ACB incoming busbar | L1 | 1 | 120 |  |  | 90
11 |  | L2 | 1 | 111 |  |  | 90
12 |  | L3 | 1 | 118 |  |  | 90
13 | Incoming terminal of 1200A ACB | L1 | 1 | 114 |  |  | 80
14 |  | L2 | 1 | 117 |  |  | 80
15 |  | L3 | 1 | 113 |  |  | 80
16 | Outgoing terminal of 1200A ACB | L1 | 1 | 115 |  |  | 80
17 |  | L2 | 1 | 116 |  |  | 80
18 |  | L3 | 1 | 119 |  |  | 80
19 | Bolted joint at CT chamber busbar | L1 | 1 | 210 |  |  | 90
20 |  | L2 | 1 | 106 |  |  | 90
21 |  | L3 | 1 | 203 |  |  | 90
22 | Bolted joint at CT chamber busbar | L1 | 1 | 209 |  |  | 90
23 |  | L2 | 1 | 208 |  |  | 90
24 |  | L3 | 1 | 202 |  |  | 90
25 | Bolted joint between CT chamber busbar busbar and horizontal busbar | L1 | 1 | 205 |  |  | 90
26 |  | L2 | 1 | 206 |  |  | 90
27 |  | L3 | 1 | 201 |  |  | 90
28 | Support of horizontal busbar | L1 | 1 | 204 |  |  | 90
29 |  | L2 | 1 | 207 |  |  | 90
30 |  | L3 | 1 | 217 |  |  | 90
31 | Bolted joint between vertical busbar and horizontal busbar | L1 | 1 | 218 |  |  | 90
32 |  | L2 | 1 | 215 |  |  | 90
33 |  | L3 | 1 | 214 |  |  | 90
46 | Bolted joint between vertical busbar and horizontal main busbar | L1 | 1 | 311 |  |  | 90
47 |  | L2 | 1 | 319 |  |  | 90
48 |  | L3 | 1 | 312 |  |  | 90
49 | Support of horizontal main busbar | L1 | 1 | 307 |  |  | 90
50 |  | L2 | 1 | 302 |  |  | 90
51 |  | L3 | 1 | 301 |  |  | 90
52 | Bolted joint of horizontal main busbar between section A and section B | L1 | 1 | 308 |  |  | 90
53 |  | L2 | 1 | 306 |  |  | 90
54 |  | L3 | 1 | 303 |  |  | 90
55 | Bolted joint between vertical busbar and horizontal main busbar in section B | L1 | 1 | 310 |  |  | 90
56 |  | L2 | 1 | 309 |  |  | 90
57 |  | L3 | 1 | 305 |  |  | 90
58 | Bolted joint between incoming busbar of B6 400A FU and vertical busbar | L1 | 1 | 304 |  |  | 90
59 |  | L2 | 2 | 104 |  |  | 90
60 |  | L3 | 2 | 110 |  |  | 90
61 | Bolted joint between incoming busbar of B4 315A FU and vertical busbar | L1 | 2 | 205 |  |  | 90
62 |  | L2 | 2 | 219 |  |  | 90
63 |  | L3 | 2 | 217 |  |  | 90
64 | Incoming terminal of B4 315A FU | L1 | 2 | 220 |  |  | 80
65 |  | L2 | 2 | 215 |  |  | 80
66 |  | L3 | 2 | 210 |  |  | 80
67 | Outgoing terminal of B4 315A FU | L1 | 2 | 203 |  |  | 80
68 |  | L2 | 2 | 209 |  |  | 80
69 |  | L3 | 2 | 202 |  |  | 80
70 | Unit B4 Outgoing terminal | L1 | 2 | 211 |  |  | 70
71 |  | L2 | 2 | 208 |  |  | 70
72 |  | L3 | 2 | 218 |  |  | 70
73 | Bolted joint between incoming busbar of B3 125A MCCB and vertical busbar | L1 | 2 | 317 |  |  | 90
74 |  | L2 | 2 | 315 |  |  | 90
75 |  | L3 | 2 | 319 |  |  | 90
76 | Incoming terminal of B3 125A MCCB | L1 | 2 | 320 |  |  | 80
77 |  | L2 | 2 | 313 |  |  | 80
78 |  | L3 | 2 | 312 |  |  | 80
79 | Outgoing terminal of B3 125A MCCB | L1 | 2 | 314 |  |  | 80
80 |  | L2 | 3 | 102 |  |  | 80
81 |  | L3 | 2 | 318 |  |  | 80
82 | Unit B3 Outgoing terminal | L1 | 3 | 106 |  |  | 70
83 |  | L2 | 3 | 103 |  |  | 70
84 |  | L3 | 2 | 204 |  |  | 70
97 | Incoming terminal of B6 400A FU | L1 | 2 | 118 |  |  | 80
98 |  | L2 | 2 | 115 |  |  | 80
99 |  | L3 | 2 | 109 |  |  | 80
100 | Outgoing terminal of B6 400A FU | L1 | 2 | 101 |  |  | 80
101 |  | L2 | 2 | 102 |  |  | 80
102 |  | L3 | 2 | 113 |  |  | 80
103 | Bolted joint between outgoing busbar of B6 400A FU and horizontal busbar | L1 | 2 | 117 |  |  | 90
104 |  | L2 | 2 | 106 |  |  | 90
105 |  | L3 | 2 | 120 |  |  | 90
106 | Bolted joint between horizontal busbar and incoming busbar of C6 400A QS | L1 | 2 | 212 |  |  | 90
107 |  | L2 | 2 | 201 |  |  | 90
108 |  | L3 | 2 | 213 |  |  | 90
109 | Incoming terminal of C6 400A QS | L1 | 3 | 118 |  |  | 80
110 |  | L2 | 3 | 116 |  |  | 80
111 |  | L3 | 3 | 114 |  |  | 80
112 | Outgoing terminal of C6 400A QS | L1 | 3 | 113 |  |  | 80
113 |  | L2 | 3 | 117 |  |  | 80
114 |  | L3 | 3 | 112 |  |  | 80
115 | Support of C6 400A QS outgoing busbar | L1 | 3 | 209 |  |  | 90
116 |  | L2 | 3 | 202 |  |  | 90
117 |  | L3 | 3 | 210 |  |  | 90
118 | Bolted joint between horizontal busbar and outgoing busbar of C6 400A QS | L1 | 3 | 115 |  |  | 90
119 |  | L2 | 3 | 120 |  |  | 90
120 |  | L3 | 3 | 111 |  |  | 90
121 | Incoming terminal of C4 400A CONTACTOR(normally close) | L1 | 3 | 108 |  |  | 65
122 |  | L2 | 3 | 316 |  |  | 65
123 |  | L3 | 3 | 110 |  |  | 65
124 | Outgoing terminal of C4 400A CONTACTOR(normally close) | L1 | 3 | 206 |  |  | 65
125 |  | L2 | 3 | 203 |  |  | 65
126 |  | L3 | 3 | 205 |  |  | 65
127 | Bolted joint between horizontal busbar and outgoing busbar of C4 400A CONTACTOR (normally close) | L1 | 3 | 201 |  |  | 90
128 |  | L2 | 3 | 204 |  |  | 90
129 |  | L3 | 3 | 207 |  |  | 90
130 | Incoming terminal of C2 400A QS | L1 | 3 | 217 |  |  | 80
131 |  | L2 | 3 | 214 |  |  | 80
132 |  | L3 | 3 | 213 |  |  | 80
133 | Outgoing terminal of C2 400A QS | L1 | 3 | 220 |  |  | 80
134 |  | L2 | 3 | 218 |  |  | 80
135 |  | L3 | 3 | 215 |  |  | 80
154 | Bolted joint of horizontal busbar between section C and section D | L1 | 3 | 211 |  |  | 90
155 |  | L2 | 4 | 111 |  |  | 90
156 |  | L3 | 4 | 101 |  |  | 90
157 | Bolted joint between vertical busbar and horizontal busbar in section D | L1 | 4 | 208 |  |  | 90
158 |  | L2 | 4 | 203 |  |  | 90
159 |  | L3 | 4 | 206 |  |  | 90
160 | Support of vertical busbar | L1 | 4 | 209 |  |  | 90
161 |  | L2 | 4 | 319 |  |  | 90
162 |  | L3 | 4 | 317 |  |  | 90
163 | Bolted joint between incoming busbar of D2 250A MCCB and vertical busbar | L1 | 4 | 110 |  |  | 90
164 |  | L2 | 4 | 106 |  |  | 90
165 |  | L3 | 4 | 113 |  |  | 90
166 | Incoming terminal of D2 250A MCCB | L1 | 4 | 115 |  |  | 80
167 |  | L2 | 4 | 120 |  |  | 80
168 |  | L3 | 4 | 109 |  |  | 80
169 | Outgoing terminal of D2 250A MCCB | L1 | 4 | 103 |  |  | 80
170 |  | L2 | 4 | 114 |  |  | 80
171 |  | L3 | 4 | 118 |  |  | 80
172 | Unit D2 Outgoing terminal | L1 | 4 | 306 |  |  | 70
173 |  | L2 | 4 | 307 |  |  | 70
174 |  | L3 | 4 | 302 |  |  | 70
199 | Enclosure of A2 | - | 5 | 111 |  |  | 30
201 | Enclosure of B6 | - | 5 | 118 |  |  | 30
202 | Enclosure of B4 | - | 5 | 213 |  |  | 30
208 | Enclosure of C2 | - | 5 | 114 |  |  | 30
209 | Enclosure of D2 | - | 5 | 219 |  |  | 30
212 | Handle of ACB | - | 5 | 105 |  |  | 25
213 | ACB OFF button | - | 5 | 106 |  |  | 40
215 | Handle of B6 | - | 5 | 116 |  |  | 25
216 | Handle of B4 | - | 5 | 210 |  |  | 25
222 | Handle of C2 | - | 5 | 115 |  |  | 25
223 | Handle of D2 | - | 5 | 204 |  |  | 25
226 | Ambient 1 | - | 5 | 206 |  |  | Ref ℃
227 | Ambient 2 | - | 5 | 209 |  |  | Ref ℃